|  | ......................... pcs. .............................. € .............................. € GEZE IO 420 interface module Module for connecting non bus-capable devices via input and output terminals or CAN-Bus to BACnet MS/TP. Top hat rail housing plastic for installation in the switch cabinet or false ceiling Supports the BACnet Standardized Device Profile BASC 4 integrated relays, each with a potential-free changeover contact for carrying out switching functions 4 integrated inputs for the release of switching functions and/or the placement of messages Interface for connection to the BUS system of GEZE swing door drives or sliding door drives Configuration of the settings via the GEZE ST 220 service terminal Adjustable module types for flexible connection of various products and warranty of the related function Connection between the interface modules via RS485 interface in line topology Connection of up to 31 devices per MS/TP segment The wiring must meet the BACnet and MS/TP EIA-485 network standard and be specified as follows: Shielded cable, pair-wise twisted. Impedance 100-130 Ohm. Capacity between the wires < 100 pF/m (30 pF/ft). Capacity between the wire and the shield < 200 pF/m (60 pF/ft). The maximum length of any individual segment is 900 m (AWG18 cable; wire cross-section 0.82 mm²). With large cable lengths, an amplifier may have to be integrated in the bus to guarantee function. Technical data: Dimensions 107 x 111 x 59 mm (W x H x D) Operating voltage 24 V DC Operating temperature -20 to +80 °C LEDs 1(red), 2(yellow), 3(red), 4(green), 5(green), 6(yellow), in(green), out(red) Interfaces CAN Bus ST 220 (GEZE parameter setting tool) GEZE Bus 2 BACnet RS485 4 inputs 4 outputs Dip switches CAN terminating resistor 120 Ohm BACnet terminating resistor 120 Ohm GEZE bus terminating resistor 120 Ohm Network bias Micro SD card FAT16/32 file format for setting parameters and changing settings via PC Reset push button to reset factory settings |
| --- | --- |
|  | ......................... pcs. .............................. € .............................. € Configuration of the new IO 420 interface module ( ) Connecting an automatic door via the input and output contacts Exchange of data via BACnet MS/TP with building automation software incl. the following functions: Feedback of modes of operation Operation of modes of operation Status change door release/open and short-term release Status feedback door open/closed, locked, unlocked Setting of full and reduced opening width ( ) Connecting an automatic door via CAN Bus. Exchange of data via BACnet MS/TP with building automation software incl. the following functions: Feedback of modes of operation Operation of modes of operation Status change door release/open and short-term release Status feedback door open/closed, locked, unlocked Setting of full and reduced opening width Feedback of all event and error and fault messages in running text ( ) Connection of a revolving door Exchange of data via BACnet MS/TP with building automation software incl. the following functions: Feedback of modes of operation Operation of modes of operation Feedback of all event and error and fault messages in running text ( ) Connection of an emergency exit system terminal Exchange of data via BACnet MS/TP with building automation software incl. the following functions: Status change door release/open and short-term release Status feedback door release, short-term release, assured Status feedback door open / closed Qualified emergency exit system reports ( ) Connection of an automatic door drive and emergency exit system terminal via a BUS system Exchange of data via BACnet MS/TP with building automation software incl. the following functions: Status change door release/open and short-term release (emergency exit system) Status feedback door release, short-term release, assured (emergency exit system) Status feedback door open / closed Qualified emergency exit system reports (emergency exit system) Feedback of modes of operation Operation of modes of operation Feedback of all event and error and fault messages in running text ( ) Connection of an automatic window drive Exchange of data via BACnet MS/TP with building automation software incl. the following functions: Status change open, close, stop window Status feedback door open, closed ( ) Connection of a hold-open system Exchange of data via BACnet MS/TP with building automation software incl. the following functions: Status feedback door open/closed Status change close door ( ) Connection of a fail-secure electric strike Exchange of data via BACnet MS/TP with building automation software incl. the following functions: Status feedback door open/closed Status change open door, close door, short-term release ( ) Connection of a fail-safe electric strike Exchange of data via BACnet MS/TP with building automation software incl. the following functions: Status feedback door open/closed Status change open door, close door, short-term release ( ) Connection of an electric lock/electromechanical lock Exchange of data via BACnet MS/TP with building automation software incl. the following functions: Status feedback door open/closed Status change open door, close door, short-term release |